## Ark1
BDK-Kraft ANDST + 17 Stk. + 2 OLTC + Ud Reserve

## Samle Ark4
| Sample object | Transformator
| Manufacturer | Strömberg
| Serial nr. | 5800657
| Product type | KYRT 170 x 23
| Voltage (kV) | 150 kV
Voltage tap 1
Voltage tap 2
| Power | 18 MVA
Power tap 1
Power tap 2
| Year of manufacture |  | Serie nr. | IEC 60422-2013 | 5800657 | 5800656 | 5800036 | 5800037 | 5800760 | 5800761 | 5800926 | 5800925 | 5800924 | 5800923 | 5800072 | 5800073 | 5800762 | 5800763 | 5801023
| Energised without load |  | Oil Quality |  | ?? ?? | ?? ?? | NT 20 X | NT 20 X | NS 10X | NS 10X | Nytro 10X | Nytro 10X | Nytro 10X | Nytro 10X | NT 20 X | NT 20 X | NS 10X | ?? ?? | ?? ??
|  |  | Oil Weight |  | 12.600 kg | 12.600 kg | 13.300 kg | 13.300 kg | 12.600 kg | 12.600 kg | 12.600 kg | 12.600 kg | 12.600 kg | 12.600 kg | 13.300 kg | 13.300 kg | 12.600 kg | 12.600 Kg | 10.300 kg
| Analysis result |  | Manf. Year + Voltage |  | 1993(22-10-1996) | 1991(08-01-1997) | 1983-02-03 | 1983-01-14 | 1993-04-14 | 1993-04-15 | 1995-08-16 | 1995-08-15 | 1994-12-14 | 1994-12-13 | 1983-03-25 | 1983-03-24 | 1997(14-09-1993) | 1996-10-21(1993) | 1996-09-18
|  |  | Sub St. ID |  | FGD KT3C | FGD KT3D | HEJ SGF T25 | HEJ SGF T26 | IGF T25 | IGF T26 | KAS JKF KT31 | KAS JKF KT32 | MAG OJF KT33 | MAG OJF KT34 | ROF T25 | ROF T26 | RYT FAF KT33 | RYT FAF KT34 | SØN SDBF KT33
| Sample date |  |  |  | 2016-04-21 | 2016-04-21 | 2016-05-27 | 2016-05-27 | 2016-06-28 | 2016-06-28 | 2015-12-08 | 2015-12-08 | 2015-12-08 | 2015-12-08 | 2016-06-30 | 2016-06-30 | 2016-06-08 | 2016-06-08 | 2015-12-07
| Prov nr. |  |  |  | 16-02311 | 16-02310 | 16-02636 | 16-02637 | 16-03185 | 16-03186 | 15-05078 | 15-05077 | 15-05081 | 15-05080 | 16-03187 | 16-03188 | 16-02689 | 16-02690 | 15-05079
| Sample place |  |  |  | Botten | Botten | - | - | Botten | Botten | Botten | Botten | Botten | Botten | Botten | Botten | Botten | Botten | Mitten
| Analysis | Norm | Unit
| Oil temperature |  | °C |  | 22 | 22 | 30 | 35 | 30 | 32 | 8 | 7 | 10 | 7 | 18 | 17 | 30 | 31 | 9
| Water content | IEC 60814 | mg/kg | from 2010 | 3 (2015) | 3 (2015) | 5 (2014) | 4 (2014) | 5 (2010) | 3 (2010) | 2 (2014) | 2 (2014) | 3 (2014) | 2 (2014) | 5 (2010) | 3 (2010) | 3 (2014) | 3 (2014) | 2 (2014)
| Insulation water content |  | %(w/w) |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Acidity | IEC 62021-1 | mg KOH/g |  | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | <0.01
| Dielectic strength | IEC 60156/95 | kV/2.5 mm |  | 82 | 82 | 76 | 70 | 55 | 79 | 97 | 98 | 94 | 69 | 66 | 75 | 72 | 75 | 86
| Acidity | IEC 62021-2 | mg KOH/g |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Dielectic strength1 | IEC 156/95 | kV/2.5 mm |  | 97 | 75 | 93 | 81 | 67 | 86 | 99 | 99 | 100 | 80 | 70 | 72 | 94 | 96 | 98
| Dielectic strength2 | IEC 156 | kV/2.5 mm |  | 86 | 77 | 85 | 65 | 50 | 94 | 87 | 100 | 81 | 65 | 68 | 81 | 83 | 71 | 99
| Dielectic strength3 | IEC 156 | kV/2.5 mm |  | 80 | 67 | 76 | 71 | 67 | 75 | 100 | 100 | 100 | 69 | 61 | 67 | 29 | 65 | 91
| Dielectic strength4 | IEC 156 | kV/2.5 mm |  | 74 | 95 | 88 | 68 | 51 | 59 | 100 | 100 | 92 | 70 | 80 | 77 | 88 | 76 | 70
| Dielectic strength5 | IEC 156 | kV/2.5 mm |  | 84 | 91 | 70 | 65 | 44 | 93 | 100 | 100 | 99 | 67 | 65 | 86 | 71 | 78 | 65
| Dielectic strength6 | IEC 156 | kV/2.5 mm |  | 70 | 85 | 42 | 72 | 50 | 69 | 99 | 87 | 93 | 64 | 56 | 67 | 70 | 67 | 91
| Standard deviation |  |  |  | 9 | 11 | 18 | 6 | 10 | 14 | 5 | 5 | 7 | 6 | 8 | 7 | 24 | 11 | 14
| Colour | ASTM D1500 |  |  | 0.5 | <0.5 | 0.5 | 1.0 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | 1.0 | 1.0 | <0.5 | <0.5 | <0.5
| Visual inspection | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Tan delta | IEC 60247 | x10-3 |  | <1 | 1 | 1 | 1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 1 | <1 | <1
| Resistivity+ 90C | IEC 60247 | G ohmm |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Resistivity- 90C | IEC 247 | G ohmm |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Interfacial tension | ASTM D971-99 | mN/m |  | 45 | 45 | 44 | 43 | 46 | 46 | 49 | 48 | 48 | 47 | 42 | 44 | 46 | 46 | 48
| Inhibitor1 | IEC 60666 | % (w/w) |  | 0.32 | 0.33 | 0.32 | 0.32 | 0.34 | 0.34 | 0.32 | 0.32 | 0.33 | 0.33 | 0.29 | 0.30 | 0.33 | 0.33 | 0.33
| Inhibitorh | CRC | % |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Inhibitor2 | CRC | % |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Passivator, Irgamet 39 | IEC 60666 | ppm |  | - | - | 1 | 1 | - | - | - | - | - | - | <1 | <1 | - | - | -
| S8 (ECD) | GC-ECD | mg/kg |  | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | - | - | - | - | <0.5 | <0.5 | <0.5 | <0.5 | -
| DBDS (ECD) | GC-ECD | mg/kg |  | 86 (2016) | 81 (2016) | <1 | <1 | 104 | 107 | 36 | 47.1 | 55.3 | 56.5 | <1 | <1 | 85 | 89 | 89.2
| CCD-C | IEC 62535 |  |  | korr | korr | ej korr | ej korr | korr(2016) | korr(2016) | Korr | Korr | Korr | Korr | korr(2015) | korr(2015) | korr | korr | Korr
| CCD | New method |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Korrosivt svavel | ASTM D1275B |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Corrosive Sulfur | DIN 51353 | - | SILVER | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr | ej korr
| DP | IEC 60450 |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Fra 2010 | 2FAL | IEC 61198 | µg/g |  | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010)
Fra 2010 | 2ACF | IEC 61198 | µg/g |  | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010)
Fra 2010 | 2FOL | IEC 61198 | µg/g |  | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010)
Fra 2010 | 5MEF | IEC 61198 | µg/g |  | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010) | <0.05 (2015) | <0.05 (2015) | <0.05 (2010) | <0.05 (2010) | <0.05 (2010)
| Density | ISO 3675 | g/cm³ |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Rapid oxidation | Rancimat B | h |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Sulphur content | CSM | mg/kg |  | 180 | 100 | 580 | 750 | 50 | 60 | - | - | - | - | 590 | 600 | 220 | 90 | -
| Viscosity +40 C | ISO 3104 | cSt |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Copper content |  | mg/kg |  | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | <0.02 | - | - | - | - | <0.02 | <0.02 | <0.02 | <0.02 | -
| PCB |  | mg/kg |  | - | - | - | - | <2 | <2 | - | - | - | - | <2 | <2 | - | - | -
| Sludge | IEC 422:89 | % (w/w) |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Flash point (Closed cup) | ISO 2719 | °C |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Hydrogen (H2) | IEC 60567 | µl/l |  | 14 | 11 | <3 | <3 | <3 | 3 | 7 | 7 | 6 | 10 | <3 | <3 | <3 | <3 | <3
| Oxygen (O2) | IEC 60567 | µl/l |  | 30000 | 31000 | 29000 | 30000 | 28000 | 30000 | 30000 | 28000 | 29000 | 28000 | 30000 | 30000 | 28000 | 28000 | 29000
| Nitrogen (N2) | IEC 60567 | µl/l |  | 68000 | 71000 | 60000 | 62000 | 62000 | 68000 | 68000 | 63000 | 66000 | 61000 | 65000 | 65000 | 60000 | 61000 | 62000
| Methane (CH4) | IEC 60567 | µl/l |  | 2 | 2 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 2 | 2 | 2
| Carbon monoxide (CO) | IEC 60567 | µl/l |  | 120 | 104 | 18 | 18 | 98 | 115 | 118 | 116 | 112 | 131 | 21 | 23 | 127 | 109 | 89
| Carbon dioxide (CO2) | IEC 60567 | µl/l |  | 803 | 851 | 680 | 663 | 879 | 1070 | 943 | 967 | 937 | 954 | 656 | 674 | 859 | 792 | 1080
| Ethene (C2H4) | IEC 60567 | µl/l |  | 2 | 3 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 3 | 2 | <1
| Ethane (C2H6) | IEC 60567 | µl/l |  | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | 3 | 3 | <1 | <1 | <1
| Acetylene (C2H2) | IEC 60567 | µl/l |  | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
| Propane (C3H8) | IEC 60567 | µl/l |  | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
| Propene (C3H6) | IEC 60567 | µl/l |  | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1 | <1
| Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Iso-Butane (C4H10) | IEC 60567 | µl/l |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| TCG | IEC 60567 | µl/l |  | 138 | 120 | 19 | 19 | 100 | 120 | 127 | 125 | 120 | 143 | 25 | 27 | 132 | 113 | 91
| TGC |  | % (v/v) |  | 10.3 | 10.7 | 9.34 | 9.66 | 9.48 | 10.3 | 10.3 | 9.59 | 10.0 | 9.39 | 9.97 | 9.97 | 9.27 | 9.37 | 9.60
| Pour point | ISO 3016 | °C |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Pour point | ASTMD5950-02 | °C |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
| Analysis date |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | -
Note on AA67: Andreas Danielsen: Se rapport 30-06-2014 14-02909 Botten H2 = 18 PPM

## FGD KT3C
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | FGD
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | KT3C
Serial nr. | 5800657 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 170 x 23 | Type of OLTC/De-energised TC | M1 351 110/C | Other information | -
Voltage (kV) | 150 kV | Manufacturer of OLTC/De-energised TC | - | Other info | Antal kopplingar 64649 den 10/4-14
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1993 | Trafo application | Feeder Traction | Project name | -
Energised without load
Analysis result
Sample date |  |  | 2016-04-21 | 2015-05-29 | 2014-09-18 | 2014-04-02 | 2014-04-02 | 2010-01-20 | 2010-01-20
Prov nr. |  |  | 16-02311 | 15-03101 | 14-04151 | 14-01813 | 14-01410 | [M] S1006869-00 | [M] S1006868-00
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 22 | 26 | 32 | - | 20 | 28 | 30
Water content | IEC 60814 | mg/kg | - | 3 | - | - | 1 | 5 | 1
Insulation water content |  | %(w/w) | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | - | <0.01 | - | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 82 | 86 | - | - | 73 | 77 | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 97 | 91 | - | - | 82 | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 86 | 84 | - | - | 71 | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 80 | 87 | - | - | 70 | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 74 | 86 | - | - | 77 | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 84 | 81 | - | - | 66 | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 70 | 86 | - | - | 70 | - | -
Standard deviation |  |  | 9 | 3 | - | - | 6 | 7 | -
Colour | ASTM D1500 |  | 0.5 | <0.5 | - | - | <0.5 | <0.5 | -
Visual inspection | - | - | - | - | - | - | - | u.a. | u.a.
Tan delta | IEC 60247 | x10-3 | <1 | <1 | - | - | <1 | 1 | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 45 | 44 | - | - | 45 | 44 | 41
Inhibitor1 | IEC 60666 | % (w/w) | 0.32 | 0.28 | - | - | 0.31 | 0.32 | 0.30
Inhibitorh | CRC | % | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | <1 | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 86 | - | - | - | 87 | - | -
CCD-C | IEC 62535 |  | korr | - | - | - | korr | Korr | -
CCD | New method |  | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | ej korr | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
2ACF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
2FOL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
5MEF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 180 | - | - | - | - | - | 185
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 14 | 13 | 13 | - | 13 | 9 | 7
Oxygen (O2) | IEC 60567 | µl/l | 30000 | 30000 | 28000 | - | 29000 | 29000 | 27250
Nitrogen (N2) | IEC 60567 | µl/l | 68000 | 66000 | 62000 | - | 63000 | 58700 | 60300
Methane (CH4) | IEC 60567 | µl/l | 2 | 1 | 1 | - | 1 | 12 | 1
Carbon monoxide (CO) | IEC 60567 | µl/l | 120 | 121 | 121 | - | 112 | 92 | 125
Carbon dioxide (CO2) | IEC 60567 | µl/l | 803 | 867 | 899 | - | 763 | 669 | 560
Ethene (C2H4) | IEC 60567 | µl/l | 2 | 2 | 2 | - | 2 | 8 | 1
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | 1 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | 2 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 138 | 137 | 137 | - | 128 | - | -
TGC |  | % (v/v) | 10.3 | 10.1 | 9.48 | - | 9.68 | 8.8 | 8.8
Pour point | ISO 3016 | °C | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | -

## FGD KT3D
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | FGD
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | KT3D
Serial nr. | 5800656 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 170 x 23 | Type of OLTC/De-energised TC | M1 351 110/C | Other information | -
Voltage (kV) | 150 kV | Manufacturer of OLTC/De-energised TC | - | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1991 | Trafo application | Feeder Traction | Project name | -
Energised without load
Analysis result
Sample date |  |  | 2016-04-21 | 2015-05-29 | 2014-09-18 | 2014-04-02 | 2014-04-02 | 2010-06-14 | 2010-01-20
Prov nr. |  |  | 16-02310 | 15-03102 | 14-04150 | 14-01812 | 14-01409 | [M] S1006871-00 | [M] S1006870-00
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 22 | 22 | 32 | - | 18 | 26 | -
Water content | IEC 60814 | mg/kg | - | 3 | - | - | 1 | 4 | -
Insulation water content |  | %(w/w) | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | 0.01 | - | - | <0.01 | - | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 82 | 74 | - | - | 96 | 85 | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 75 | 98 | - | - | 99 | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 77 | 76 | - | - | 99 | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 67 | 71 | - | - | 100 | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 95 | 68 | - | - | 98 | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 91 | 69 | - | - | 97 | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 85 | 63 | - | - | 85 | - | -
Standard deviation |  |  | 11 | 12 | - | - | 6 | 12 | -
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | - | <0.5 | <0.5 | -
Visual inspection | - | - | - | - | - | - | - | u.a. | -
Tan delta | IEC 60247 | x10-3 | 1 | <1 | - | - | <1 | 1 | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 45 | 45 | - | - | 42 | 44 | 41
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.28 | - | - | 0.31 | 0.32 | 0.29
Inhibitorh | CRC | % | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | <1 | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 81 | - | - | - | 82 | - | -
CCD-C | IEC 62535 |  | korr | - | - | - | korr | Korr | -
CCD | New method |  | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | ej korr | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
2ACF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
2FOL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
5MEF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 100 | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 11 | 11 | 10 | - | 11 | 6 | 13
Oxygen (O2) | IEC 60567 | µl/l | 31000 | 30000 | 28000 | - | 28000 | 28700 | 28850
Nitrogen (N2) | IEC 60567 | µl/l | 71000 | 64000 | 63000 | - | 60000 | 56500 | 60450
Methane (CH4) | IEC 60567 | µl/l | 2 | 1 | 1 | - | 1 | 0 | 2
Carbon monoxide (CO) | IEC 60567 | µl/l | 104 | 106 | 106 | - | 95 | 76 | 110
Carbon dioxide (CO2) | IEC 60567 | µl/l | 851 | 892 | 916 | - | 751 | 601 | 555
Ethene (C2H4) | IEC 60567 | µl/l | 3 | 2 | 2 | - | 1 | 3 | 1
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | 1 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | <1 | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 120 | 120 | 119 | - | 108 | - | -
TGC |  | % (v/v) | 10.7 | 9.90 | 9.59 | - | 9.26 | 8.6 | <9.0
Pour point | ISO 3016 | °C | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | -

## HEJ SGF T25
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | Hejninge
Manufacturer | Strömberg | Oil weight | 13300 kg | Local identity | SGF T25
Serial nr. | 5800036 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 145*23 | Type of OLTC/De-energised TC | MR MI 301110/C16151W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info | LK kopplat 1984 ggr pr. 2014.06.30.
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1983 | Trafo application | Feeder Traction | Project name | -
Energised without load
Analysis result
Sample date |  |  | 2016-05-27 | 2015-12-28 | 2015-12-28 | 2014-06-30 | 2014-06-30 | 2010-06-14 | 2009-11-20 | 2006-07-01
Prov nr. |  |  | 16-02636 | 16-00219 | 16-00089 | 14-02905 | 14-03755 | [M] S1006900-00 | [M] S1006899-00 | [M] S1006898-00
Sample place |  |  | - | Top | Top | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 30 | - | 20 | 42 | - | 40 | 40 | 40
Water content | IEC 60814 | mg/kg | - | - | - | 5 | - | 5 | - | -
Insulation water content |  | %(w/w) | - | - | - | ca 1.5 | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | - | <0.01 | <0.01 | 0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 76 | - | 79 | 91 | - | 57 | - | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 93 | - | 84 | 100 | - | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 85 | - | 81 | 99 | - | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 76 | - | 81 | 95 | - | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 88 | - | 80 | 88 | - | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 70 | - | 85 | 82 | - | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 42 | - | 64 | 81 | - | - | - | -
Standard deviation |  |  | 18 | - | 8 | 8 | - | 11 | - | -
Colour | ASTM D1500 |  | 0.5 | - | 1.0 | 0.5 | - | 1.0 | - | -
Visual inspection | - | - | - | - | - | - | - | u.a. | - | -
Tan delta | IEC 60247 | x10-3 | 1 | - | <1 | 1 | - | 2 | - | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 44 | - | 44 | 44 | - | 43 | 42 | 41
Inhibitor1 | IEC 60666 | % (w/w) | 0.32 | - | 0.31 | 0.30 | - | 0.34 | 0.28 | 0.29
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | 1 | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | <1 | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | ej korr | - | - | - | - | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | - | - | ej korr | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 580 | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3 | 9 | - | 0 | <5 | 8
Oxygen (O2) | IEC 60567 | µl/l | 29000 | - | 30000 | 31300 | - | 29800 | 29950 | 32350
Nitrogen (N2) | IEC 60567 | µl/l | 60000 | - | 64000 | 66400 | - | 58000 | 61000 | 65600
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1 | <1 | - | 0 | 1 | 1
Carbon monoxide (CO) | IEC 60567 | µl/l | 18 | - | 19 | 20 | - | 14 | 40 | 28
Carbon dioxide (CO2) | IEC 60567 | µl/l | 680 | - | 681 | 698 | - | 619 | 575 | 610
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 3 | 0 | 0
Ethane (C2H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 1 | 0 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 19 | - | 20 | 30 | - | - | - | -
TGC |  | % (v/v) | 9.34 | - | 9.87 | 10.25 | - | 8.8 | <9.2 | <9.9
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## HEJ SGF T26
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | Hejninge
Manufacturer | Strömberg | Oil weight | 13300 kg | Local identity | SGF T26
Serial nr. | 5800037 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 145*23 | Type of OLTC/De-energised TC | MR MI 301110/C16151W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info | Lk kopplat 1339 ggr pr. 2014.06.30
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1983 | Trafo application | Feeder Traction | Project name | -
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-05-27 | 2015-12-28 | 2015-12-28 | 2014-06-30 | 2014-06-30 | 2010-06-15 | 2009-11-20 | 2006-07-01
Prov nr. |  |  | 16-02637 | 16-00220 | 16-00090 | 14-02906 | 14-03756 | [M] S1006903-00 | [M] S1006902-00 | [M] S1006901-00
Sample place |  |  | - | Top | Top | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 35 | - | 20 | 30 | - | 32 | 10 | 48
Water content | IEC 60814 | mg/kg | - | - | - | 4 | - | 5 | - | -
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | - | <0.01 | <0.01 | 0.02
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 70 | - | 70 | 88 | - | 82 | - | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 81 | - | 64 | 90 | - | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 65 | - | 65 | 85 | - | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 71 | - | 75 | 100 | - | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 68 | - | 70 | 85 | - | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 65 | - | 67 | 73 | - | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 72 | - | 79 | 95 | - | - | - | -
Standard deviation |  |  | 6 | - | 6 | 10 | - | 9 | - | -
Colour | ASTM D1500 |  | 1.0 | - | 1.0 | 0.5 | - | 1.0 | - | -
Visual inspection | - | - | - | - | - | - | - | u.a. | - | -
Tan delta | IEC 60247 | x10-3 | 1 | - | 1 | 1 | - | 1 | - | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 43 | - | 44 | 43 | - | 43 | 41 | 41
Inhibitor1 | IEC 60666 | % (w/w) | 0.32 | - | 0.31 | 0.30 | - | 0.34 | 0.24 | 0.25
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | 1 | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | <1 | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | ej korr | - | - | - | - | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | - | - | ej korr | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | - | - | - |  | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | - | - | - | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 750 | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3 | 13 | - | 2 | 5 | 9
Oxygen (O2) | IEC 60567 | µl/l | 30000 | - | 29000 | 31500 | - | 27400 | 29450 | 31740
Nitrogen (N2) | IEC 60567 | µl/l | 62000 | - | 60000 | 66300 | - | 52000 | 59250 | 64030
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1 | <1 | - | 0 | 2 | 1
Carbon monoxide (CO) | IEC 60567 | µl/l | 18 | - | 20 | 20 | - | 15 | 35 | 30
Carbon dioxide (CO2) | IEC 60567 | µl/l | 663 | - | 653 | 689 | - | 549 | 555 | 615
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 2 | 0 | 0
Ethane (C2H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 0 | 0 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 19 | - | 21 | 33 | - | - | - | -
TGC |  | % (v/v) | 9.66 | - | 9.34 | 10.26 | - | 8.0 | <8.9 | <9.6
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## IGF T25
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Nynäs Nytro 10X | Location at present | IGF
Manufacturer | ABB Strömberg | Oil weight | 12600 kg | Local identity | IGF T25
Serial nr. | 5800760 | Type of tap changer | Lindningkopplare | Owner | BDK-Kraft
Product type | KYRT 145+23 | Type of OLTC/De-energised TC | M1 351 130C 16151W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info | LK tillv.nr.189095. Prover finns.
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1 | Fläktar monterade 2010.
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 23 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN/ONAF | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1993 | Trafo application | Feeder Traction | Project name | -
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-28 | 2015-01-16 | 2014-10-06 | 2010-06-04 | 2007-06-19 | 2007-06-19
Prov nr. |  |  | 16-03185 | 15-00520 | 14-04363 | [M] S1006856-00 | [M] S1002757-00 | [M] S1002758-00
Sample place |  |  | Botten | Botten | - | Botten | Botten | Topp
Analysis | Norm | Unit
Oil temperature |  | °C | 30 | 20 | 20 | 26 | 23 | 23
Water content | IEC 60814 | mg/kg | - | - | - | 5 | 13 | 6
Insulation water content |  | %(w/w) | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | <0.01 | <0.01 | <0.01 | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 55 | 100 | 100 | 93 | 87 | 95
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 67 | 99 | 99 | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 50 | 100 | 99 | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 67 | 99 | 99 | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 51 | 100 | 99 | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 44 | 100 | 100 | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 50 | 9 | 101 | - | - | -
Standard deviation |  |  | 10 | 1 | 1 | 6 | 7 | 8
Colour | ASTM D1500 |  | <0.5 | <0.5 | <0.5 | <0.5 | <0.5 | -
Visual inspection | - | - | - | - | - | u.a. | u.a. | -
Tan delta | IEC 60247 | x10-3 | <1 | 1 | 5 | 1 | 1 | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 46 | 47 | 48 | 45 | 45 | -
Inhibitor1 | IEC 60666 | % (w/w) | 0.34 | 0.36 | 0.36 | 0.34 | 0.31 | -
Inhibitorh | CRC | % | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | <0.5 | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 104 | - | 109 | - | - | -
CCD-C | IEC 62535 |  | korr | Korr | - | Korr | Korr | -
CCD | New method |  | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | ej korr | - | - | -
DP | IEC 60450 |  | - | - | - |  | - | -
2FAL | IEC 61198 | µg/g | - | <0.05 | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | <0.05 | - | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | <0.05 | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | <0.05 | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 50 | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | <0.02 | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | 4 | <3 | 3 | 4 | 4
Oxygen (O2) | IEC 60567 | µl/l | 28000 | 28000 | 28000 | 29000 | 23200 | 23900
Nitrogen (N2) | IEC 60567 | µl/l | 62000 | 62000 | 62000 | 59300 | 57700 | 57800
Methane (CH4) | IEC 60567 | µl/l | 2 | 2 | 2 | 0 | 1 | 1
Carbon monoxide (CO) | IEC 60567 | µl/l | 98 | 111 | 120 | 107 | 97 | 91
Carbon dioxide (CO2) | IEC 60567 | µl/l | 879 | 830 | 1010 | 696 | 560 | 549
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | <1 | 2 | 1 | 0
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | <1 | 1 | 0 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | <1 | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 100 | 117 | 122 | - | - | -
TGC |  | % (v/v) | 9.48 | 9.47 | 9.49 | 8.9 | 8.2 | 8.2
Pour point | ISO 3016 | °C | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | -

## IGF T26
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Nynäs Nytro 10X | Location at present | IGF
Manufacturer | ABB Strömberg | Oil weight | 12600 kg | Local identity | IGF T26
Serial nr. | 5800761 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 145X23 | Type of OLTC/De-energised TC | MI 351-110/C-16151 W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info | Lindningskopplare snr 189096
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1 | Antal kopplingar sept 2014: 1936
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2 | Fläktar monterade 2010
Power | 23 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN/ONAF | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1993 | Trafo application | Feeder Traction | Project name | -
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-28 | 2016-06-28 | 2015-01-16 | 2014-09-23 | 2010-06-15 | 2007-06-21 | 2007-06-21
Prov nr. |  |  | 16-03186 | 16-03754 | 15-00521 | 14-04148 | [M] S1006855-00 | [M] S1002759-00 | [M] S1002760-00
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | Botten | Topp
Analysis | Norm | Unit
Oil temperature |  | °C | 32 | - | 19 | 14 | 18 | 21 | 21
Water content | IEC 60814 | mg/kg | - | - | - | - | 3 | 8 | 7
Insulation water content |  | %(w/w) | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | <0.01 | <0.01 | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 79 | - | 82 | 76 | 95 | 86 | 93
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 86 | - | 84 | 100 | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 94 | - | 86 | 99 | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 75 | - | 69 | 77 | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 59 | - | 85 | 31 | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 93 | - | 92 | 49 | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 69 | - | 75 | 100 | - | - | -
Standard deviation |  |  | 14 | - | 8 | 30 | 13 | 7 | 10
Colour | ASTM D1500 |  | <0.5 | - | <0.5 | <0.5 | <0.5 | <0.5 | -
Visual inspection | - | - | - | - | - | - | u.a. | u.a. | -
Tan delta | IEC 60247 | x10-3 | <1 | - | 1 | 1 | 1 | 1 | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 46 | - | 48 | 48 | 44 | 46 | -
Inhibitor1 | IEC 60666 | % (w/w) | 0.34 | - | 0.35 | 0.35 | 0.34 | 0.33 | -
Inhibitorh | CRC | % | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | <0.5 | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 107 | - | - | 108 | - | - | -
CCD-C | IEC 62535 |  | korr | - | korr | - | Korr | Korr | -
CCD | New method |  | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | - | ej korr | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | <0.05 | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | - | <0.05 | - | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | - | <0.05 | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | - | <0.05 | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 60 | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | <0.02 | - | - | - | -
PCB |  | mg/kg | - | <2 | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 3 | - | 4 | 4 | 3 | 0 | 5
Oxygen (O2) | IEC 60567 | µl/l | 30000 | - | 28000 | 28200 | 30875 | 23100 | 24300
Nitrogen (N2) | IEC 60567 | µl/l | 68000 | - | 61000 | 63100 | 64515 | 56500 | 60800
Methane (CH4) | IEC 60567 | µl/l | 2 | - | 2 | 2 | 0 | 1 | 2
Carbon monoxide (CO) | IEC 60567 | µl/l | 115 | - | 107 | 110 | 99 | 84 | 96
Carbon dioxide (CO2) | IEC 60567 | µl/l | 1070 | - | 842 | 906 | 639 | 436 | 953
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | <1 | 3 | 0 | 0
Ethane (C2H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | 1 | 0 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | <1 | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 120 | - | 113 | 116 | - | - | -
TGC |  | % (v/v) | 10.3 | - | 9.37 | 9.62 | 9.6 | 8.0 | 8.6
Pour point | ISO 3016 | °C | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | -

## KAS JKF KT31
Laboratory report
Oil/gas anlysis
Sample object | Transfomator | Oil type | - | Location at present | KAS
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | JKF KT31
Serial nr. | 5800926 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1995 | Trafo application | Feeder Traction | Project name
Energised without load | 1995 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-06-02 | 2009-04-06 | 2009-04-06 | 2006-11-06 | 2006-11-06
Prov nr. |  |  | 15-05078 | 14-02910 | 14-03760 | [M] S1006867-00 | 09-01970 | [M] S1006866-00 | 06-03989 | [M] S1006865-00
Sample place |  |  | Botten | Botten | Botten | Botten | - | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 8 | 33 | - | 28 | - | - | 23 | 23
Water content | IEC 60814 | mg/kg | - | 2 | - | 3 | - | - | 1 | 1
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | <0.01 | - | - | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 97 | 83 | - | 79 | - | - | 72 | 72
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 99 | 97 | - | - | - | - | 77 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 87 | 89 | - | - | - | - | 78 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 100 | 90 | - | - | - | - | 70 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 100 | 76 | - | - | - | - | 72 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 100 | 77 | - | - | - | - | 73 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 99 | 69 | - | - | - | - | 60 | -
Standard deviation |  |  | 5 | 11 | - | 11 | - | - | 7 | 7
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | <0.5 | - | - | <0.5 | <0.5
Visual inspection | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | 0.3 | - | 4 | - | - | 2 | 2
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 49 | 47 | - | 46 | - | - | 49 | 49
Inhibitor1 | IEC 60666 | % (w/w) | 0.32 | 0.32 | - | 0.32 | - | - | 0.31 | 0.31
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | - | - | - | Korr | Korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | <0.05 |  | - | - | -
2FOL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 7 | 11 | - | 3 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 30000 | 30500 | - | 30600 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 68000 | 66400 | - | 64800 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 1 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 118 | 93 | - | 85 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 943 | 823 | - | 691 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | - | 3 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 127 | 106 | - | - | - | - | - | -
TGC |  | % (v/v) | 10.3 | 10.19 | - | 9.6 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## KAS JKF KT32
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | KAS
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | JKF KT32
Serial nr. | 5800925 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1995 | Trafo application | Feeder Traction | Project name
Energised without load
Analysis result
Sample date |  |  | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-06-02 | 2009-04-06 | 2009-04-06 | 2006-11-06 | 2006-11-06
Prov nr. |  |  | 15-05077 | 14-02911 | 14-03761 | [M] S1006864-00 | 09-01972 | [M] S1006863-00 | 06-03996 | [M] S1006862-00
Sample place |  |  | Botten | Botten | Botten | Botten | - | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 7 | 32 | - | 28 | - | - | 25 | 25
Water content | IEC 60814 | mg/kg | - | 2 | - | 4 | - | - | 1 | 1
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | <0.01 | - | - | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 98 | 100 | - | 84 | - | - | 76 | 76
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 99 | 100 | - | - | - | - | 91 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 100 | 99 | - | - | - | - | 76 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 100 | 99 | - | - | - | - | 75 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 100 | 100 | - | - | - | - | 66 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 100 | 101 | - | - | - | - | 75 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 87 | 100 | - | - | - | - | 74 | -
Standard deviation |  |  | 5 | 1 | - | 15 | - | - | 8 | 8
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | <0.5 | - | - | <0.5 | <0.5
Visual inspection | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | 0.3 | - | 1 | - | - | 2 | 2
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 48 | 48 | - | 44 | - | - | 48 | 48
Inhibitor1 | IEC 60666 | % (w/w) | 0.32 | 0.31 | - | 0.32 | - | - | 0.31 | 0.31
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | - | - | - | Korr | Korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 7 | 15 | - | 4 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 28000 | 30200 | - | 29300 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 63000 | 65800 | - | 63400 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 1 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 116 | 93 | - | 89 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 967 | 846 | - | 698 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | - | 3 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | - | 1 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 125 | 109 | - | - | - | - | - | -
TGC |  | % (v/v) | 9.59 | 10.10 | - | 9.3 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## MAG OJF KT33
Laboratory report
Oil/gas anlysis
Sample object | Transfomator | Oil type | - | Location at present | MAG
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | OJF KT33
Serial nr. | 5800924 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1994 | Trafo application | Feeder Traction | Project name
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-06-02 | 2009-04-03 | 2009-04-03 | 2006-11-06 | 2006-11-06
Prov nr. |  |  | 15-05081 | 14-02907 | 14-03757 | [M] S1006874-00 | 09-01978 | [M] S1006873-00 | 06-03997 | [M] S1006872-00
Sample place |  |  | Botten | Botten | Botten | Botten | - | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 10 | 28 | - | 28 | - | - | 22 | 22
Water content | IEC 60814 | mg/kg | - | 3 | - | 4 | - | - | 1 | 1
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | <0.01 | - | - | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 94 | 59 | - | 69 | - | - | 82 | 82
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 100 | 72 | - | - | - | - | 78 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 81 | 41 | - | - | - | - | 84 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 100 | 91 | - | - | - | - | 81 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 92 | 38 | - | - | - | - | 83 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 99 | 35 | - | - | - | - | 80 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 93 | 77 | - | - | - | - | 84 | -
Standard deviation |  |  | 7 | 24 | - | 8 | - | - | 3 | 3
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | <0.5 | - | - | <0.5 | <0.5
Visual inspection | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | <1 | - | 1 | - | - | 1 | 1
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 48 | 47 | - | 43 | - | - | 47 | 47
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.32 | - | 0.32 | - | - | 0.32 | 0.32
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | - | - | - | Korr | korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - |  | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 6 | 14 | - | 4 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 29000 | 30000 | - | 27900 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 66000 | 65900 | - | 56700 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 1 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 112 | 89 | - | 90 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 937 | 812 | - | 598 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | - | 2 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 120 | 104 | - | - | - | - | - | -
TGC |  | % (v/v) | 10.0 | 10.09 | - | 8.5 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## MAG OJF KT34
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | MAG
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | OJF KT34
Serial nr. | 5800923 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1994 | Trafo application | Feeder Traction | Project name
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-01-09 | 2009-04-03 | 2009-04-03 | 2006-11-06 | 2006-11-06
Prov nr. |  |  | 15-05080 | 14-02909 | 14-03759 | [M] S1006877-00 | 09-01973 | [M] S1006876-00 | 06-03991 | [M] S1006875-00
Sample place |  |  | Botten | Botten | Botten | Botten | - | - | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 7 | 30 | - | 28 | - | - | 24 | 24
Water content | IEC 60814 | mg/kg | - | 2 | - | 4 | - | - | 2 | 2
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | <0.01 | - | - | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 69 | 76 | - | 77 | - | - | 90 | 90
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 80 | 96 | - | - | - | - | 90 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 65 | 86 | - | - | - | - | 94 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 69 | 82 | - | - | - | - | 93 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 70 | 70 | - | - | - | - | 82 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 67 | 80 | - | - | - | - | 85 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 64 | 43 | - | - | - | - | 93 | -
Standard deviation |  |  | 6 | 19 | - | 19 | - | - | 5 | 5
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | <0.5 | - | - | <0.5 | <0.5
Visual inspection | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | <1 | - | 1 | - | - | 1 | 1
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 47 | 48 | - | 46 | - | - | 49 | 49
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.32 | - | 0.32 | - | - | 0.32 | 0.32
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | - | - | - | Korr | Korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | 10 | 18 | - | 2 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 28000 | 31200 | - | 27000 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 61000 | 68300 | - | 53700 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 2 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 131 | 105 | - | 108 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 954 | 855 | - | 695 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | - | 4 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | - | 1 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 143 | 125 | - | - | - | - | - | -
TGC |  | % (v/v) | 9.39 | 10.47 | - | 8.2 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## OKF T25
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | NYNAS LYRA X | Location at present | OKF
Manufacturer | CG Electric Systems; Ungarn | Oil weight | 13 500 kg | Local identity | OKF T25
Serial nr. | 136826 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | EOS 23000/145 | Type of OLTC/De-energised TC | MI 351-245/B-16151WR | Other information | -
Voltage (kV) | 145/26 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info | Signal/alarm från Hydrocal 2014-07-25
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 23 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 2011 | Trafo application | Feeder Traction | Project name | -
Energised without load | 2011 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-07-01 | 2016-07-01 | 2015-01-16 | 2014-07-30 | 2014-07-30
Prov nr. |  |  | 16-03189 | 16-03757 | 15-00522 | 14-03182 | 14-03896
Sample place |  |  | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 17 | - | 11 | 20 | -
Water content | IEC 60814 | mg/kg | - | - | - | 3 | -
Insulation water content |  | %(w/w) | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 69 | - | 89 | 75 | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 68 | - | 99 | 68 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 62 | - | 96 | 69 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 71 | - | 87 | 74 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 70 | - | 82 | 79 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 72 | - | 82 | 78 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 70 | - | 87 | 82 | -
Standard deviation |  |  | 4 | - | 7 | 6 | -
Colour | ASTM D1500 |  | 0.5 | - | 0.5 | 0.5 | -
Visual inspection | - | - | - | - | - | - | -
Tan delta | IEC 60247 | x10-3 | 1 | - | 4 | 3 | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 39 | - | 40 | 40 | -
Inhibitor1 | IEC 60666 | % (w/w) | 0.31 | - | 0.33 | 0.28 | -
Inhibitorh | CRC | % | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | <0.5 | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | <1 | - | -
CCD-C | IEC 62535 |  | - | - | ej korr | - | -
CCD | New method |  | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | - |  | ej korr
DP | IEC 60450 |  | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | - | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | -
PCB |  | mg/kg | - | <2 | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3 | <3 | -
Oxygen (O2) | IEC 60567 | µl/l | 29000 | - | 28000 | 31000 | -
Nitrogen (N2) | IEC 60567 | µl/l | 66000 | - | 60000 | 67000 | -
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1 | <1 | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 65 | - | 61 | 64 | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 540 | - | 388 | 423 | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | <1 | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | <1 | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | <1 | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | <1 | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | -
TCG | IEC 60567 | µl/l | 66 | - | 62 | 65 | -
TGC |  | % (v/v) | 9.96 | - | 9.21 | 10.3 | -
Pour point | ISO 3016 | °C | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | -
Analysis date |  |  | - | - | - | - | -

## OKF T26
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Nynas Lyra X | Location at present | OKF
Manufacturer | CG Electric Systems; Ungarn | Oil weight | 13500 kg | Local identity | OKF T26
Serial nr. | 136827 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | EOS 23000/145 | Type of OLTC/De-energised TC | MI 351-245/B-16151WR | Other information | -
Voltage (kV) | 145/26 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 23 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 2011 | Trafo application | Feeder Traction | Project name | -
Energised without load | 2011 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-07-01 | 2016-07-01 | 2015-01-16
Prov nr. |  |  | 16-03190 | 16-03758 | 15-00523
Sample place |  |  | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 30 | - | 12
Water content | IEC 60814 | mg/kg | - | - | -
Insulation water content |  | %(w/w) | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 93 | - | 77
Acidity | IEC 62021-2 | mg KOH/g | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 99 | - | 78
Dielectic strength2 | IEC 156 | kV/2.5 mm | 93 | - | 80
Dielectic strength3 | IEC 156 | kV/2.5 mm | 99 | - | 60
Dielectic strength4 | IEC 156 | kV/2.5 mm | 82 | - | 92
Dielectic strength5 | IEC 156 | kV/2.5 mm | 87 | - | 85
Dielectic strength6 | IEC 156 | kV/2.5 mm | 95 | - | 68
Standard deviation |  |  | 7 | - | 12
Colour | ASTM D1500 |  | 0.5 | - | 0.5
Visual inspection | - | - | - | - | -
Tan delta | IEC 60247 | x10-3 | 1 | - | 2
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 38 | - | 39
Inhibitor1 | IEC 60666 | % (w/w) | 0.29 | - | 0.32
Inhibitorh | CRC | % | - | - | -
Inhibitor2 | CRC | % | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | <0.5
DBDS (ECD) | GC-ECD | mg/kg | - | - | <1
CCD-C | IEC 62535 |  | - | - | ej korr
CCD | New method |  | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr
DP | IEC 60450 |  | - | - | -
2FAL | IEC 61198 | µg/g | - | - | <0.05
2ACF | IEC 61198 | µg/g | - | - | <0.05
2FOL | IEC 61198 | µg/g | - | - | <0.05
5MEF | IEC 61198 | µg/g | - | - | <0.05
Density | ISO 3675 | g/cm³ | - | - | -
Rapid oxidation | Rancimat B | h | - | - | -
Sulphur content | CSM | mg/kg | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | -
Copper content |  | mg/kg | - | - | -
PCB |  | mg/kg | - | <2 | -
Sludge | IEC 422:89 | % (w/w) | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3
Oxygen (O2) | IEC 60567 | µl/l | 28000 | - | 28000
Nitrogen (N2) | IEC 60567 | µl/l | 60000 | - | 61000
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1
Carbon monoxide (CO) | IEC 60567 | µl/l | 68 | - | 72
Carbon dioxide (CO2) | IEC 60567 | µl/l | 607 | - | 427
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1
Ethane (C2H6) | IEC 60567 | µl/l | <1 | - | <1
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | -
TCG | IEC 60567 | µl/l | 69 | - | 73
TGC |  | % (v/v) | 9.24 | - | 9.32
Pour point | ISO 3016 | °C | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | -
Analysis date |  |  | - | - | -

## ROF T25
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Mineralolja | Location at present | ROF
Manufacturer | ABB Strömberg | Oil weight | 13300 kg | Local identity | ROF T25
Serial nr. | 5800072 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 145*23 | Type of OLTC/De-energised TC | MI 301-110/C-16151W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1983 | Trafo application | Feeder Traction | Project name | -
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-30 | 2016-06-30 | 2015-01-14 | 2010-06-14 | 2009-11-20 | 2008-11-19 | 2006-10-05 | 2004-04-14 | 1989-12-04
Prov nr. |  |  | 16-03187 | 16-03755 | 15-00518 | [M] S1006892-00 | [M] S1006891-00 | [M] S1006890-00 | [M] S1006889-00 | [M] S1006888-00 | 90-00017
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | - | Botten | Botten | -
Analysis | Norm | Unit
Oil temperature |  | °C | 18 | - | 16 | 28 | 25 | - | 27 | 25 | -
Water content | IEC 60814 | mg/kg | - | - | - | 5 | - | - | - | - | -
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | <0.01 | - | - | - | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 66 | - | 96 | 74 | - | - | - | - | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 70 | - | 83 | - | - | - | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 68 | - | 99 | - | - | - | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 61 | - | 99 | - | - | - | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 80 | - | 98 | - | - | - | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 65 | - | 96 | - | - | - | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 56 | - | 100 | - | - | - | - | - | -
Standard deviation |  |  | 8 | - | 6 | 4 | - | - | - | - | -
Colour | ASTM D1500 |  | 1.0 | - | 1.0 | 1.0 | - | - | - | - | -
Visual inspection | - | - | - | - | - | u.a. | - | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | - | 2 | 1 | - | - | - | - | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 42 | - | 42 | 42 | 41 | - | - | - | -
Inhibitor1 | IEC 60666 | % (w/w) | 0.29 | - | 0.31 | 0.34 | 0.13 | - | - | - | -
Inhibitorh | CRC | % | - | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | <1 | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | <0.5 | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | <1 | - | <1 | - | - | - | - | - | -
CCD-C | IEC 62535 |  | korr | - | korr | Korr | - | - | - | - | -
CCD | New method |  | - | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | ej korr | - | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 590 | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | <2 | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3 | 5 | 8 | <5 | <5 | <5 | 1
Oxygen (O2) | IEC 60567 | µl/l | 30000 | - | 28000 | 36200 | 29600 | 29900 | 31350 | 27300 | 29505
Nitrogen (N2) | IEC 60567 | µl/l | 65000 | - | 59000 | 89000 | 60300 | 61550 | 64850 | 58100 | 57424
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1 | 0 | 1 | 2 | 1 | 1 | 2
Carbon monoxide (CO) | IEC 60567 | µl/l | 21 | - | 23 | 203 | 40 | 35 | 30 | 23 | 41
Carbon dioxide (CO2) | IEC 60567 | µl/l | 656 | - | 573 | 634 | 485 | 500 | 605 | 451 | 427
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | 2 | 0 | - | 0 | 0 | 0
Ethane (C2H6) | IEC 60567 | µl/l | 3 | - | <1 | 0 | 0 | 0 | 0 | 0 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | 0 | 0 | 0 | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | 2
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | 0
TCG | IEC 60567 | µl/l | 25 | - | 24 | - | - | - | - | - | 46
TGC |  | % (v/v) | 9.97 | - | 9.13 | 12.6 | 9.0 | - | <9.7 | <8.6 | 9.18
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | - | -

## ROF T26
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Nynäs Nytro 10X | Location at present | ROF
Manufacturer | ABB Strömberg | Oil weight | 13300 kg | Local identity | ROF T26
Serial nr. | 5800073 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT 145*23 | Type of OLTC/De-energised TC | MI 301-110/C-16151 W | Other information | -
Voltage (kV) | 132 kV | Manufacturer of OLTC/De-energised TC | Reinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1983 | Trafo application | Feeder Traction | Project name | -
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-30 | 2016-06-30 | 2015-01-15 | 2010-06-04 | 2009-11-20 | 2008-10-27 | 2006-10-05 | 2004-04-14 | 1989-12-04
Prov nr. |  |  | 16-03188 | 16-03756 | 15-00519 | [M] S1006897-00 | [M] S1006896-00 | [M] S1006895-00 | [M] S1006894-00 | [M] S1006893-00 | 90-00018
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | Botten | Botten | Botten | -
Analysis | Norm | Unit
Oil temperature |  | °C | 17 | - | 16 | 34 | 30 | - | 25 | 26 | -
Water content | IEC 60814 | mg/kg | - | - | - | 3 | - | - | - | - | -
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | - | <0.01 | <0.01 | 0.01 | 0.01 | - | 0.01 | -
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 75 | - | 88 | 77 | - | - | - | - | -
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 72 | - | 95 | - | - | - | - | - | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 81 | - | 87 | - | - | - | - | - | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 67 | - | 83 | - | - | - | - | - | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 77 | - | 84 | - | - | - | - | - | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 86 | - | 79 | - | - | - | - | - | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 67 | - | 98 | - | - | - | - | - | -
Standard deviation |  |  | 7 | - | 7 | 7 | - | - | - | - | -
Colour | ASTM D1500 |  | 1.0 | - | 1.0 | 1.0 | - | - | - | - | -
Visual inspection | - | - | - | - | - | u.a. | - | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | - | 1 | 1 | - | - | - | - | -
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 44 | - | 43 | 43 | 41 | 40 | - | 39 | -
Inhibitor1 | IEC 60666 | % (w/w) | 0.30 | - | 0.31 | 0.34 | 0.27 | 0.29 | - | 0.33 | -
Inhibitorh | CRC | % | - | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | <1 | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | <0.5 | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | <1 | - | <1 | - | - | - | - | - | -
CCD-C | IEC 62535 |  | korr | - | korr | Korr | - | - | - | - | -
CCD | New method |  | - | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | ej korr | - | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | <0.05 | <0.05 | - | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 600 | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | <2 | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | - | <3 | 1 | <5 | <5 | <5 | <5 | 8
Oxygen (O2) | IEC 60567 | µl/l | 30000 | - | 28000 | 28900 | 30050 | 28550 | 31000 | 16300 | 29615
Nitrogen (N2) | IEC 60567 | µl/l | 65000 | - | 58000 | 56400 | 61500 | 58650 | 64700 | 62500 | 58029
Methane (CH4) | IEC 60567 | µl/l | 1 | - | 1 | 0 | 2 | 1 | 1 | 3 | 3
Carbon monoxide (CO) | IEC 60567 | µl/l | 23 | - | 24 | 18 | 40 | 35 | 30 | 70 | 46
Carbon dioxide (CO2) | IEC 60567 | µl/l | 674 | - | 618 | 501 | 530 | 510 | 660 | 1200 | 303
Ethene (C2H4) | IEC 60567 | µl/l | <1 | - | <1 | 0 | 0 | 0 | 0 | 1 | 0
Ethane (C2H6) | IEC 60567 | µl/l | 3 | - | <1 | 0 | 0 | 0 | 0 | 2 | 0
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | - | <1 | 0 | 0 | 0 | 0 | 0 | 0
Propane (C3H8) | IEC 60567 | µl/l | <1 | - | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | - | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | 0
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | 0
TCG | IEC 60567 | µl/l | 27 | - | 25 | - | - | - | - | - | 57
TGC |  | % (v/v) | 9.97 | - | 9.03 | 8.6 | <9.2 | <8.8 | <9.6 | <8.0 | 9.4
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | - | -

## RYT FAF KT33
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | RYT
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | FAF KT33
Serial nr. | 5800762 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1993 | Trafo application | Feeder Traction | Project name
Energised without load | 1993 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-08 | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-06-03 | 2006-11-09 | 2006-11-09
Prov nr. |  |  | 16-02689 | 15-05082 | 14-02913 | 14-03763 | [M] S1006861-00 | 06-03982 | [M] S1006860-00
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 30 | 8 | 28 | - | 16 | 18 | 18
Water content | IEC 60814 | mg/kg | - | - | 3 | - | 3 | 2 | 2
Insulation water content |  | %(w/w) | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | <0.01 | - | <0.01 | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 72 | 97 | 88 | - | 75 | 75 | 75
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 94 | 84 | 100 | - | - | 82 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 83 | 100 | 71 | - | - | 73 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 29 | 99 | 92 | - | - | 63 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 88 | 100 | 92 | - | - | 85 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 71 | 100 | 81 | - | - | 72 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 70 | 100 | 94 | - | - | 76 | -
Standard deviation |  |  | 24 | 6 | 11 | - | 13 | 8 | 8
Colour | ASTM D1500 |  | <0.5 | <0.5 | 0.5 | - | <0.5 | <0.5 | <0.5
Visual inspection | - | - | - | - | - | - | u.a. | - | -
Tan delta | IEC 60247 | x10-3 | 1 | <1 | <1 | - | 1 | 5 | 5
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 46 | 44 | 45 | - | 43 | 46 | 46
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.31 | 0.31 | - | 0.32 | 0.31 | 0.31
Inhibitorh | CRC | % | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 85 | - | - | - | - | - | -
CCD-C | IEC 62535 |  | korr | - | - | - | Korr | korrosiv | Korr
CCD | New method |  | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | - | ej korr | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | -
2ACF | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | -
2FOL | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | -
5MEF | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 220 | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | 4 | <3 | - | 3 | - | -
Oxygen (O2) | IEC 60567 | µl/l | 28000 | 28000 | 29700 | - | 29200 | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 60000 | 62000 | 66100 | - | 62500 | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 2 | 1 | - | 0 | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 127 | 164 | 122 | - | 104 | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 859 | 932 | 813 | - | 691 | - | -
Ethene (C2H4) | IEC 60567 | µl/l | 3 | 3 | 2 | - | 4 | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | 1 | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | <1 | - | 0 | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 132 | 173 | 128 | - | - | - | -
TGC |  | % (v/v) | 9.27 | 9.49 | 10.07 | - | 9.3 | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | -

## RYT FAF KT34
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | RYT
Manufacturer | Strömberg | Oil weight | 12600 kg | Local identity | FAF KT34
Serial nr. | 5800763 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x23 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 18 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object | -
Year of manufacture | 1993 | Trafo application | Feeder Traction | Project name
Energised without load | - | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-06-08 | 2015-12-08 | 2014-06-30 | 2014-06-30 | 2010-06-01 | 2009-04-02 | 2009-04-02 | 2006-11-09 | 2006-11-09
Prov nr. |  |  | 16-02690 | 15-05083 | 14-02908 | 14-03758 | [M] S1006859-00 | 09-01971 | [M] S1006858-00 | 06-03990 | [M] S1006857-00
Sample place |  |  | Botten | Botten | Botten | Botten | Botten | - | botten | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 31 | 7 | 30 | - | 31 | - | - | 20 | 20
Water content | IEC 60814 | mg/kg | - | - | 3 | - | 4 | - | - | 2 | 2
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | 0.01 | <0.01 | - | <0.01 | - | - | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 75 | 96 | 94 | - | 92 | - | - | 86 | 86
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 96 | 99 | 99 | - | - | - | - | 98 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 71 | 99 | 87 | - | - | - | - | 87 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 65 | 100 | 98 | - | - | - | - | 89 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 76 | 1000 | 92 | - | - | - | - | 74 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 78 | 95 | 89 | - | - | - | - | 84 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 67 | 84 | 97 | - | - | - | - | 87 | -
Standard deviation |  |  | 11 | 6 | 5 | - | 5 | - | - | 8 | 8
Colour | ASTM D1500 |  | <0.5 | <0.5 | <0.5 | - | <0.5 | - | - | <0.5 | <0.5
Visual inspection | - | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | <1 | <1 | - | 1 | - | - | 1 | 1
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 46 | 45 | 46 | - | 44 | - | - | 49 | 49
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.31 | 0.31 | - | 0.32 | - | - | 0.31 | 0.31
Inhibitorh | CRC | % | - | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | <0.5 | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | 89 | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | korr | - | - | - | Korr | Korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | ej korr | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | 90 | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | <0.02 | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | <3 | 10 | - | 3 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 28000 | 28000 | 29700 | - | 29000 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 61000 | 63000 | 64500 | - | 61500 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 2 | 1 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 109 | 140 | 110 | - | 92 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 792 | 871 | 780 | - | 615 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | 2 | 2 | 1 | - | 3 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | 1 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | <1 | - | 1 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 113 | 144 | 123 | - | - | - | - | - | -
TGC |  | % (v/v) | 9.37 | 9.59 | 9.91 | - | 9.1 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | - | -

## SØN SDBF KT33
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | - | Location at present | SØN
Manufacturer | Strömberg | Oil weight | 10300 kg | Local identity | SDBF KT33
Serial nr. | 5801023 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | KYRT170x10 | Type of OLTC/De-energised TC | MRMI | Other information | -
Voltage (kV) | 150/26 kV | Manufacturer of OLTC/De-energised TC | Rheinhausen | Other info
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Öppet | Other info 2
Power | 7.5 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | ONAN | Other info 4
Power tap 2 |  | Number of phases | 2 | Failure in object
Year of manufacture | 1996 | Trafo application | Feeder Traction | Project name
Energised without load | 1996 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2015-12-07 | 2014-07-01 | 2014-06-30 | 2010-06-02 | 2009-03-16 | 2009-03-16 | 2006-11-06 | 2006-11-06
Prov nr. |  |  | 15-05079 | 14-02912 | 14-03762 | [M] S1006906-00 | 09-01087 | [M] S1006905-00 | 06-03994 | [M] S1006904-00
Sample place |  |  | Mitten | Botten | Botten | Botten | Lock | Lock | Botten | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 9 | 32 | - | 30 | 20 | 20 | 25 | 25
Water content | IEC 60814 | mg/kg | - | 2 | - | 4 | 2 | 2 | 1 | 1
Insulation water content |  | %(w/w) | - | - | - | - | - | - | - | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01 | <0.01 | - | - | <0.01 | <0.01 | <0.01 | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 86 | 85 | - | 98 | 97 | 97 | 88 | 88
Acidity | IEC 62021-2 | mg KOH/g | - | - | - | - | - | - | - | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 98 | 78 | - | - | 100 | - | 100 | -
Dielectic strength2 | IEC 156 | kV/2.5 mm | 99 | 96 | - | - | 99 | - | 100 | -
Dielectic strength3 | IEC 156 | kV/2.5 mm | 91 | 84 | - | - | 100 | - | 98 | -
Dielectic strength4 | IEC 156 | kV/2.5 mm | 70 | 70 | - | - | 99 | - | 44 | -
Dielectic strength5 | IEC 156 | kV/2.5 mm | 65 | 97 | - | - | 94 | - | 92 | -
Dielectic strength6 | IEC 156 | kV/2.5 mm | 91 | 86 | - | - | 91 | - | 86 | -
Standard deviation |  |  | 14 | 10 | - | 6 | 4 | 4 | 22 | 22
Colour | ASTM D1500 |  | <0.5 | <0.5 | - | <0.5 | <0.5 | <0.5 | <0.5 | <0.5
Visual inspection | - | - | - | - | - | u.a. | - | - | - | -
Tan delta | IEC 60247 | x10-3 | <1 | <1 | - | 1 | 1 | 1 | 1 | 1
Resistivity+ 90C | IEC 60247 | G ohmm | - | - | - | - | - | - | - | -
Resistivity- 90C | IEC 247 | G ohmm | - | - | - | - | - | - | - | -
Interfacial tension | ASTM D971-99 | mN/m | 48 | 49 | - | 47 | 53 | 53 | 49 | 49
Inhibitor1 | IEC 60666 | % (w/w) | 0.33 | 0.33 | - | 0.33 | 0.32 | 0.32 | 0.32 | 0.32
Inhibitorh | CRC | % | - | - | - | - | - | - | - | -
Inhibitor2 | CRC | % | - | - | - | - | - | - | - | -
Passivator, Irgamet 39 | IEC 60666 | ppm | - | - | - | - | - | - | - | -
S8 (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
DBDS (ECD) | GC-ECD | mg/kg | - | - | - | - | - | - | - | -
CCD-C | IEC 62535 |  | - | - | - | Korr | Korrosiv | Korr | - | -
CCD | New method |  | - | - | - | - | - | - | - | -
Korrosivt svavel | ASTM D1275B |  | - | - | - | - | - | - | - | -
Corrosive Sulfur | DIN 51353 | - | - | - | ej korr | - | - | - | - | -
DP | IEC 60450 |  | - | - | - | - | - | - | - | -
2FAL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2ACF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
2FOL | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
5MEF | IEC 61198 | µg/g | - | - | - | <0.05 | - | - | - | -
Density | ISO 3675 | g/cm³ | - | - | - | - | - | - | - | -
Rapid oxidation | Rancimat B | h | - | - | - | - | - | - | - | -
Sulphur content | CSM | mg/kg | - | - | - | - | - | - | - | -
Viscosity +40 C | ISO 3104 | cSt | - | - | - | - | - | - | - | -
Copper content |  | mg/kg | - | - | - | - | - | - | - | -
PCB |  | mg/kg | - | - | - | - | - | - | - | -
Sludge | IEC 422:89 | % (w/w) | - | - | - | - | - | - | - | -
Flash point (Closed cup) | ISO 2719 | °C | - | - | - | - | - | - | - | -
Hydrogen (H2) | IEC 60567 | µl/l | <3 | <3 | - | 5 | - | - | - | -
Oxygen (O2) | IEC 60567 | µl/l | 29000 | 30200 | - | 28600 | - | - | - | -
Nitrogen (N2) | IEC 60567 | µl/l | 62000 | 64600 | - | 55300 | - | - | - | -
Methane (CH4) | IEC 60567 | µl/l | 2 | 2 | - | 0 | - | - | - | -
Carbon monoxide (CO) | IEC 60567 | µl/l | 89 | 75 | - | 59 | - | - | - | -
Carbon dioxide (CO2) | IEC 60567 | µl/l | 1080 | 973 | - | 753 | - | - | - | -
Ethene (C2H4) | IEC 60567 | µl/l | <1 | <1 | - | 2 | - | - | - | -
Ethane (C2H6) | IEC 60567 | µl/l | <1 | <1 | - | 1 | - | - | - | -
Acetylene (C2H2) | IEC 60567 | µl/l | <1 | <1 | - | 0 | - | - | - | -
Propane (C3H8) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene (C3H6) | IEC 60567 | µl/l | <1 | <1 | - | - | - | - | - | -
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | - | - | - | - | - | - | - | -
TCG | IEC 60567 | µl/l | 91 | 77 | - | - | - | - | - | -
TGC |  | % (v/v) | 9.60 | 9.99 | - | 8.5 | - | - | - | -
Pour point | ISO 3016 | °C | - | - | - | - | - | - | - | -
Pour point | ASTMD5950-02 | °C | - | - | - | - | - | - | - | -
Analysis date |  |  | - | - | - | - | - | - | - | -

## ANDST T1
Laboratory report
Oil/gas anlysis
Sample object | Transformator | Oil type | Nytro Libra + Nyhib 10 | Location at present | ANDST
Manufacturer | Siemens | Oil weight | 14250 kg | Local identity | T3
Serial nr. | 100853 | Type of tap changer | Lindningskopplare | Owner | BDK-Kraft
Product type | ESSU7552 | Type of OLTC/De-energised TC | - | Other information | -
Voltage (kV) | 165/27.5 kV | Manufacturer of OLTC/De-energised TC | - | Other info | Byte av 25 kV gnmf.+avg.olja 161128.
Voltage tap 1 |  | Connection TC/tank | Separat | Other info 1
Voltage tap 2 |  | Type of exp. vessel | Gummisäck | Other info 2
Power | 30/15/15 MVA | Type of cooler |  | Other info 3
Power tap 1 |  | Type of cooling | - | Other info 4
Power tap 2 |  | Number of phases | - | Failure in object
Year of manufacture | 2016 | Trafo application | Banmatare | Project name | -
Energised without load | 2016 | Type of regulation |  | Heat-run tests
Analysis result
Sample date |  |  | 2016-11-29
Prov nr. | View comment for sample |  | 16-05387
Sample place |  |  | Botten
Analysis | Norm | Unit
Oil temperature |  | °C | 24
Water content | IEC 60814 | mg/kg | -
Insulation water content |  | %(w/w) | -
Acidity | IEC 62021-1 | mg KOH/g | <0.01
Dielectic strength | IEC 60156/95 | kV/2.5 mm | 94
Acidity | IEC 62021-2 | mg KOH/g | -
Dielectic strength1 | IEC 156/95 | kV/2.5 mm | 96
Dielectic strength2 | IEC 156 | kV/2.5 mm | 79
Dielectic strength3 | IEC 156 | kV/2.5 mm | 100
Dielectic strength4 | IEC 156 | kV/2.5 mm | 96
Dielectic strength5 | IEC 156 | kV/2.5 mm | 100
Dielectic strength6 | IEC 156 | kV/2.5 mm | 96
Standard deviation |  |  | 8
Colour | ASTM D1500 |  | <0.5
Visual inspection | - | - | -
Tan delta | IEC 60247 | x10-3 | 2
Resistivity+ 90C | IEC 60247 | G ohmm | -
Resistivity- 90C | IEC 247 | G ohmm | -
Interfacial tension | ASTM D971-99 | mN/m | 47
Inhibitor1 | IEC 60666 | % (w/w) | 0.37
Inhibitorh | CRC | % | -
Inhibitor2 | CRC | % | -
Passivator, Irgamet 39 | IEC 60666 | ppm | -
S8 (ECD) | GC-ECD | mg/kg | <0.5
DBDS (ECD) | GC-ECD | mg/kg | <1
CCD-C | IEC 62535 |  | ej korr
CCD | New method |  | -
Korrosivt svavel | ASTM D1275B |  | -
Corrosive Sulfur | DIN 51353 | - | ej korr
DP | IEC 60450 |  | -
2FAL | IEC 61198 | µg/g | -
2ACF | IEC 61198 | µg/g | -
2FOL | IEC 61198 | µg/g | -
5MEF | IEC 61198 | µg/g | -
Density | ISO 3675 | g/cm³ | 877
Rapid oxidation | Rancimat B | h | -
Sulphur content | CSM | mg/kg | 180
Viscosity +40 C | ISO 3104 | cSt | 9.47
Copper content |  | mg/kg | -
PCB |  | mg/kg | -
Sludge | IEC 422:89 | % (w/w) | -
Flash point (Closed cup) | ISO 2719 | °C | 148
Hydrogen (H2) | IEC 60567 | µl/l | <3
Oxygen (O2) | IEC 60567 | µl/l | 2200
Nitrogen (N2) | IEC 60567 | µl/l | 7400
Methane (CH4) | IEC 60567 | µl/l | <1
Carbon monoxide (CO) | IEC 60567 | µl/l | 3
Carbon dioxide (CO2) | IEC 60567 | µl/l | 23
Ethene (C2H4) | IEC 60567 | µl/l | <1
Ethane (C2H6) | IEC 60567 | µl/l | <1
Acetylene (C2H2) | IEC 60567 | µl/l | <1
Propane (C3H8) | IEC 60567 | µl/l | <1
Propene (C3H6) | IEC 60567 | µl/l | <1
Propene + Propane (C3H6+C3H8) | IEC 60567 | µl/l | -
Iso-Butane (C4H10) | IEC 60567 | µl/l | -
TCG | IEC 60567 | µl/l | 3
TGC |  | % (v/v) | 1.00
Pour point | ISO 3016 | °C | -
Pour point | ASTMD5950-02 | °C | -
Analysis date |  |  | -
Date 2016-11-29 Sample nr. 2016-05387
Provet är taget efter att genomföring bytts ut och oljan avgasats.
OLJEKONDITION
Baserat på utförda bestämningar och befintlig information är oljan i acceptabel kondition. För densitet, viskositet samt halt av svavel, se även bifogad laboratorierapport PRR17-00639 från Exova Materials Technology AB.
TEST PÅ FÖREKOMST AV KORROSIVT SVAVEL
Oljan är icke korrosiv enligt IEC 62535. Oljan är icke korrosiv enligt (silver) DIN 51353.
GASANALYS
Resultatet visar att oljan har avgasats och tyder inte på något onormalt.
REKOMMENDATION
Oljans kondition föranleder ingen åtgärd. Nytt prov för gasanalys 1 månad efter idrifttagning. Nytt prov för kontroll av oljans kondition om 5 år.
CONTACT PERSON
Andreas Danielsen
Note on D22: anddan11: Date 2016-11-29 Sample nr. 2016-05387 Provet är taget efter att genomföring bytts ut och oljan avgasats. OLJEKONDITION Baserat på utförda bestämningar och befintlig information är oljan i acceptabel kondition. För densitet, viskositet samt halt av svavel, se även bifogad laboratorierapport PRR17-00639 från Exova Materials Technology AB. TEST PÅ FÖREKOMST AV KORROSIVT SVAVEL Oljan är icke korrosiv enligt IEC 62535. Oljan är icke korrosiv enligt (silver) DIN 51353. GASANALYS Resultatet visar att oljan har avgasats och tyder inte på något onormalt. REKOMMENDATION Oljans kondition föranleder ingen åtgärd. Nytt prov för gasanalys 1 månad efter idrifttagning. Nytt prov för kontroll av oljans kondition om 5 år. CONTACT PERSON Andreas Danielsen